## Slide 1: A Crash Course in Power Quality Issues and Monitoring
Wednesday July 24
10:30 AM - 12:00 PM
Jeff Moore, Instruments & Technology

## Slide 2: What is “Power Quality”?
Power Quality refers to how well the Voltage, Frequency & Waveform match the established specifications.
It can refer to compatibility load to the source.
It can also used to describe how the utility customer feels their needs are being met

## Slide 3: Why is it important?
Poor Power Quality is expensive!
Damaged Equipment
Unplanned Downtime
Out of spec product
Danger to personnel (elevator, fires etc.)
Environmental Hazards

## Slide 4: Where does Poor PQ come from?
Utility Transformer
  You can start here
Wiring inside the customer’s house or building
We have all see wiring that is more reminiscent of a bird’s nest that professional, modern wiring.
Devices/Equipment inside the building
Variable speed drives, computers, high-tech loads, and other internal loads cause disturbances & harmonics

## Slide 5: Key areas of Focus
Sags
Swells
Harmonics
Flicker
Transients
Grounding

## Slide 6: Voltage Swells
a.k.a. Surges
A temporary increase in voltage which lasts several cycles(1/2 cycle to 1 minute duration)
Caused by sudden changes in load or when a fault is cleared

## Slide 7: Voltage Sags
A temporary reduction in voltage.
Caused by an abrupt increase in load or a failure of utility equipment

## Slide 8: Harmonics
Harmonics are defined as Sinusoidal Voltages or Currents having frequencies that are integer multiples of the frequency (fundamental frequency = 60 Hz for NA) at which the supply system is designed to operate
Results in a distorted Waveform
Caused by VFD’s, Switching Power Supplies & Damaged Equipment

## Slide 9: Harmonics Part Deux
Negative Sequence Harmonics
5th, 11th, 17th, etc. are important to industrial environments
They are caused by electronically controlled motors.
Negative sequence harmonics counteract electrical power systems. (They make motors run backwards).
These cause motor overheating and failure.

## Slide 10: Harmonics Part Tres
Zero Sequence & Triplen Harmonics
Caused by computers and electronic equipment
3rd, 9th, 15th, etc. (div. by 3) are important to commercial environments.
Triplen Harmonics cause a disruption in the balance of a 3-phase system and cause unusually high neutral current and
causes overheating

## Slide 11: Harmonics Part Quatro
Harmonic THD or Total Harmonic Distortion
Caused by computers and electronic equipment
IEEE provides guidelines for acceptable harmonic current and voltage distortion levels.
IEEE Standard 519-1992 states that THD for critical motors should be less than 5% Voltage THD & 20% Current THD
Triplen Harmonics cause a disruption in the balance of a 3-phase system and cause unusually high neutral current and
causes overheating

## Slide 12: Flicker
A momentary or sustained fluctuation of Voltage that causes lighting to “Flicker”
Short Term Flicker(PST) is measured over 10 minutes
Long Term Flicker(PLT) is measured over 2 hours
Can cause vision trouble, headaches, annoyance & distraction
Mitigation focuses on reducing the amplitude of the voltage fluctuations

## Slide 13: Transients
Sudden brief fluctuations of voltage or current lasting only milliseconds
Caused by lightning, switching operations or faults
Typically corrected by surge suppressors

## Slide 14: Grounding & Bonding
Grounding is not a problem
Bonding is not a problem
Lack of Grounding and/or Bonding is a Huge Problem!!
Without proper Grounding & Bonding Measurement Results will be suspect & mitigation devices will not function properly
Without proper Grounding & Bonding Safety will also be compromised as protection devices will not function properly

## Slide 15: Questions?
?’s

## Slide 16: Thank You!
Contact me anytime:
INSTRUMENTS & TECHNOLOGY, INC.
Jeff Moore
700 NORTH GLENMORE STREET
LOCKPORT, IL 60441 • TEL; (815) 341-1978
jeff@instrumentsandtechnology.com