## Slide 1: Current Transformers and Ratio, Burden and Admittance Testing
July 22, 2024
1:00 PM – 2:30 PM
Rob Reese

## Slide 2: Agenda
  CT Functionality Basics
  The Faceplate: Terminology and Specifications
  Ratio Testing
  Burden Testing
  Admittance Testing

## Slide 3: Meter Forms and Applications
2S
3S
4S
5S
6S
9S
12S
15S
16S
25S
45S
10S
11S
14S
17S
32S
39S
26S
35S
46S
56S
66S
76S
1S
13S
24S

## Slide 4: Meter Forms and Applications
1S
2S
3S
4S
5S
6S
9S
12S
15S
16S
25S
45S
10S
11S
13S
14S
17S
24S
32S
39S
26S
35S
46S
56S
66S
76S
TRANSFORMER RATED
7S
8S
29S
36S
SELF-CONTAINED

## Slide 5: Self-Contained Metering
Relatively Low Current
Example: 100A
Primarily Residential
(1S, 2S, 12S)

## Slide 6: Self-Contained Metering
Primarily Residential
(1S, 2S, 12S)

## Slide 7: Transformer-Rated Metering
Relatively High Current
Example: 2000A
Primarily Commercial/Industrial

## Slide 8: Transformer-Rated Metering
Primarily Commercial/Industrial

## Slide 9: What is a CT?
“A current transformer (CT) is used for measurement of alternating electric currents. Current transformers, together with voltage (or potential) transformers (VT or PT), are known as instrument transformers. When current in a circuit is too high to apply directly to measuring instruments, a current transformer produces a reduced current accurately proportional to the current in the circuit, which can be conveniently connected to measuring and recording instruments. A current transformer isolates the measuring instruments from what may be very high voltage in the monitored circuit. Current transformers are commonly used in metering and protective relays in the electrical power industry.” - Wikipedia

## Slide 10: Current Transformers Conceptual Representation
Real, with core losses
Ideal. No losses
As current is applied in the primary, it produces a magnetic flux in the core. This flux flows through the core and induces a current in the secondary windings and circuit that is proportional to the number of turns.

## Slide 11: Example Application
9S Meter Installation
5A
PHASE A
SOURCE
PHASE C
PHASE B
LOAD
400A
400A
400A
5A
5A

## Slide 12: Faceplate Specifications

## Slide 13: Faceplate Specifications
Ratio

## Slide 14: CT’s Ratio
For instance, a CT with a 400:5 ratio will produce 5A on the secondary, when 400A are applied to the primary.
400Amps
5Amps

## Slide 15: Faceplate Specifications
Thermal factor

## Slide 16: CT’s – Functions and Terminology
Thermal Rating factor
A value representing the amount by which the primary current can be increased without exceeding the allowable temperature rise.
For instance, a RF of 4.0 at 30° ambient on a 400:5 ratio CT would allow for a primary current up to 1600A.

## Slide 17: Faceplate Specifications
Accuracy Classifications
All CT’s fall within an accuracy class.
IEEE Standards have defined accuracy classes.

## Slide 18: Faceplate Specifications
BurdenRating

## Slide 19: Burden Rating
The burden range, present in the secondary circuit, that the manufacturer will guarantee their CT’s will still accurately function, in regards to the ratio specification.

## Slide 20: Ratio Testing
Ratio of Primary Current to Secondary Current
5A
PHASE A
SOURCE
LOAD
400A
400A
400A
5A
5A
Calculate Ratio

## Slide 21: Burden Testing
Functionality with Burden Present on the Secondary Loop
PHASE A
Some burden will always be present – junctions, meter coils, test switches, cables, etc.
CT’s must be able to maintain an accurate ratio with burden on the secondary.

## Slide 22: Burden Testing
Functionality with Burden Present on the Secondary Loop
PHASE A
Some burden will always be present – junctions, meter coils, test switches, cables, etc.
CT’s must be able to maintain an accurate ratio with burden on the secondary.

## Slide 23: Burden Testing
Functionality with Burden Present on the Secondary Loop
Example Burden Spec:
0.3% @ B0.1, B0.2, B0.5
or
There should be less than the 0.3% change in secondary current from initial (“0” burden) reading, when up to 0.5Ohms of burden is applied

## Slide 24: Burden Testing
Functionality with Burden Present on the Secondary Loop
ANSI Burden Values
0.1 Ohms
0.2 Ohms
0.5 Ohms
1 Ohms
2 Ohms
4 Ohms
8 Ohms

## Slide 25: Burden Testing
Burden | Reading
0 | 5.0000
0.1 | 4.9999
0.2 | 4.9950
0.5 | 4.9900
1 | 4.9800
2 | 4.9500
4 | 4.0000
8 | 0.8000
0.3% @ B0.1, B0.2, B0.5
Initial Reading = 5Amps
0.3% x 5A = 0.015A
5A – 0.015 = 4.985A

## Slide 26: Burden Testing
Burden | Reading
0 | 5.0000
0.1 | 4.9999
0.2 | 4.9950
0.5 | 4.9900
1 | 4.9800
2 | 4.9500
4 | 4.0000
8 | 0.8000
0.3% @ B0.1, B0.2, B0.5
Initial Reading = 5Amps
0.3% x 5A = 0.015A
5A – 0.015 = 4.985A
At 0.5Ohms of Burden
the secondary current is still at 4.990A – Less than 0.3% change – Good CT!

## Slide 27: Admittance Testing
What is Admittance?
Admittance testing measures the overall “health” of the secondary loop of the CT.
Measured in units of MiliSiemens (mS)
Admittance is the inverse of impedance.
Impedance is the opposition to current.
Therefore, admittance testing measures the overall “health” of the secondary loop of the CT.

## Slide 28: Admittance Testing
Admittance testing devices inject an audio sine wave signal into the secondary loop of the CT.
The resulting current is measured.
The voltage of the initial signal is known.
From these two parameters, the impedance, and thus the admittance can be calculated.

## Slide 29: Admittance Testing
Admittance test results are not immediately intuitive.
Some analysis and interpretation is need.
What do all these mS values mean?

## Slide 30: Admittance Testing
Three phase process is recommended.
Test each CT individually
Test the matched sets
Test over time

## Slide 31: Questions and Discussion
Rob Reese
Midwestern Regional Sales Manager
rob.reese@tescometering.com
TESCO Metering Bristol, PA
215.228.0500
This presentation can also be found under Meter Conferences and Schools on the TESCO website: tescometering.com
ISO 9001:2015 Certified Quality Company
ISO 17025:2017 Accredited Laboratory