## Slide 1: Practical Use of Vectors in Electric Metering and Field Testing at Instrument Rated Services
July 23, 2024
8:45 AM -10:15 AM
Carl Chermak

## Slide 2: Symbolic Representation
Electrical Quantities are Difficult to Visualize.
Written or Spoken work is inadequate.
  Usually hard to explain in a universally understood way.
  Would take a relatively long time to explain.
Employ Vector Diagram to Represent Electrical Quantities.
  Saves time
  Vastly more effective, once it is understood
2

## Slide 3: Metering
The most basic statement of metering:
Watts = Voltage x Current x Power Factor Mathematically:
Watts  V  I  cos
What is a Vector?
A measurement that takes two numbers to represent.
BOTH a magnitude (size) and direction

## Slide 4: Origination of a Sinusoid
By Electromagnetic Induction, a single wire conductor passing through a permanent magnetic field and cutting the lines of magnetic flux, will produce an ElectroMotive Force (EMF).
Due to the constant rotation, the EMF is different at each moment in time. The instantaneous value at each moment is considered the Instantaneous Voltage.Commonly, the symbol E and V are interchanged to represent voltage values.
4
N
S
V
GENERATION OF A SINE WAVE
An Elementary Alternator
For Frequency f = 60 Hz
= 120 rads/sec
N = 3600 rpm = 60 revs/sec
Angular frequency

= 2f rads/sec
Period T = 1/f = 1/60 secs
= 16.67 msec
Ø°
N rpm
arc = a
radius = r
Ø° or

rads

= a/r = Ø°x
/
/180 radians
D.F.Bullock
6/1/95
60°
90°= /2 rads
30°
0°
V = k*Sin (Ø, or

or

t)
90
180
270
360 –– degrees
Coil Rotation Ø
°


2

–– radians
Coil Rotation, radians


k
- k
Alternator Voltage
16.67 –– milliseconds
8.33
/
2
3
/
2
Time, t

12.5
4.17
30
60
Ø
°
Rotating Coil
Reference: https://www.electronics-tutorials.ws/accircuits/sinusoidal-waveform.html

## Slide 5: “Time” in Degrees
-2
-1
0
1
2
0
30
60
90
120
150
180
210
240
270
300
330
360
Current
Voltage
Degrees
CCW
30°
6
5
Voltage
Current
Current lags Voltage by 30 degrees.
.866 PF

## Slide 6: “Time” in Degrees
-2
-1
1
0
0 30 60 90 120 150 180 210 240 270 300 330 360
Current
Voltage
Degrees
-1
0
0
1
90
180
270
Phase Angle (Degrees)
V volts or I amps
2
90°
180°
I
A
6
6
270°
I
C
I
B
EB 0°
A
E
C
B
EA
C

## Slide 7
AC Voltage and Current

## Slide 8: Vectors or Phasors are…
a Symbolic Representation of the relationship
of the voltage and current
Vectors & Vector Diagrams
  SIMPLE. Used to Represent Electrical Quantities.
  QUICK. Saves time.
  Vastly more effective
  Also referred to as “Phasors”

## Slide 9: The Phasor Diagram
A phasor diagram is a method of expressing the magnitudes and time relationships (or phase angle relationships) between two or more sinusoidal quantities of the same frequency.
Each alternating quantity having the same frequency can be represented on the same diagram by additional lines. Their time relationship will determine the angle between the lines.
The phasor diagram is a “snap-shot” of the set of lines at an instant in time. The instant is generally chosen to be the time at which the voltage passes through zero in the positive direction. If there is more than one voltage, the instant at which phase A voltage passes through zero is chosen.
Notes: Presenter
2019-08-21 16:57:42
--------------------------------------------
One Frequency, say 60 Hz, without harmonics

## Slide 10: Representing Voltage(E) & Current (I) with Lines
Vectors all have MAGNITUDE and DIRECTION
Line length can represent MAGNITUDE.
Line with arrowhead in a given direction indicates that quantity’s relationship to any other quantity being represented.
DIRECTION: Angles between lines take on significance. They represent time (shown in degrees instead of seconds).
Notes: Presenter
2019-08-21 16:57:41
--------------------------------------------
Representing Magnitude is optional and may be helpful

## Slide 11: Placing Coils in Order
and placed on an alternator in order OA, OB, and OC
(Changing Coil order changes Sequence)
120o
120o
120o
120o
120o
O
O
O
B
C
C
Coils connected together
B
Delta Connection A
O
Wye Connection
120o
A
Notes: Presenter
2019-08-21 16:57:41
--------------------------------------------
Even with labeled terminals, there is more than one way to connect the windings

## Slide 12: Drawing the Phasor
General Guidelines
Complete circle (360 Degrees) equal one cycle of the frequency displayed.
One component (Usually Phase A voltage) becomes the reference and is placed at zero degrees.
Use “open” arrowhead on voltage line(s).
Use “closed” (or filled in) arrowhead on current line(s).
Label all voltages and currents by phase.
Indicate Phase Rotation (counter-clockwise assumed if not noted).

## Slide 13: Watthour Metering
Watthour meter theory review:
– If we apply “V” volts and “I” amps to a meter, and the phase angle between the voltage and current is some angle , the meter speed will be proportional to:
Watts  V  I  cos
VECTORIALLY
V
I


## Slide 14: Analyzing the Phasor Picture
Both voltage & current are required in each meter element (stator) for that element to have an effect on registration.
Time relationship (degrees separation) between voltage & current acting together on each element will determine that element’s effect.
Only angles of less than 90 Degrees between the current and voltage on any meter element will cause positive watthour registration.
Notes: Presenter
2019-08-21 16:57:42
--------------------------------------------
Two dots and an ellipse may be added to our phasor diagram to indicate voltage and current phasors that act together in a metering element.

## Slide 15: The Phasor Diagram
16
0o
270o
90o
180o
Ena
Ia
Enc
Ib
Enb
Ic
A-B-C
Notes: Presenter
2019-08-21 16:57:42
--------------------------------------------
4 Wire Wye Service shown with balanced loading and unity power factor. A-B-C Phase Sequence.
Counter Clock-wise Phasor Rotation.
Circle is dimensioned to show how many degrees quantities lag the A-Phase Voltage.

## Slide 16: Service & Meter Phasors
Service Phasors
Meter Phasors 2 ½ Element
0o
270o
90o
180o
Ena
Ia
Enb
Ib
Enc
Ic
A-B-C
0o
270o
90o
180o
VA
Ia
Ib
VC
Ic
A-B-C
Notes: Presenter
2019-08-21 16:57:42
--------------------------------------------
If we are using a non-Blondel metering application, the meter phasors will be different than the service phasors.

## Slide 17: Load Caused Phase Angles
V
V
V
I
I
I
0
180
270
360
450
540
630
720
0
90
180
270
360
450
540
630
720
0
270
360
450
540
630
720
V
180
I90
V
I90
V
I
Notes: Presenter
2019-08-21 16:57:42
--------------------------------------------
Time Domain plots and phasor diagrams for the basic electrical components:
Resistors
Inductors
Capacitors

## Slide 18: Effect of Power Factor
We represent energy as:
 is the angle between V and I
Cos  is also known as Power Factor
What  values give with these lagging Power Factors?
Power Factor Phase Angle
0.50 | 0.70 | 0.85 | 0.90 | 0.95
60 | 45.6 | 31.8 | 25.8 | 18.2
Energy  E  I  cos   t
Notes: Presenter
2019-08-21 16:57:46
--------------------------------------------
What power factors might we encounter while verifying meter connections.
Note that even at the “good” 95% power factor, we have significant angle between the voltage and current.

## Slide 19: Three Wire Delta Source
C
B
A
EAC
EBA
ECB
ILine C
ILine A
ILine B
With pure resistance balanced three-phase load, the current in each supply transformer is in phase with the voltage across each transformer.
Notes: Presenter
2019-08-21 16:57:46
--------------------------------------------
While the meter phasors for a 4 wire wye are easily visualized, the expected phasor diagram for a 3 wire delta may be more difficult to visualize. It is worthwhile to review the phasors we expect for a 3 wire delta service.

## Slide 20: Drawing Source Phasors
ILine B
Phasor diagram for delta-connected three-phase system with three-phase delta-connected resistance load
EBA
Phase voltages = EBA, ECB, & EAC Line currents = IA, IB, & IC
C
B
A
EAC
EBA
ECB
ILine C
ILine A
I
C
EAC
ECB
(30° + )
IA
IB
(30° + )
(30° +
)
Notes: Presenter
2019-08-21 16:57:46
--------------------------------------------
The voltages are assumed to have a positive sign as they go counter clockwise around the windings. The currents are assumed to have a positive sign as they flow from the source to the load.
The C phase current is composed of a current component from the AC winding and in phase with Eac and a current component from the CB winding and in phase with Ecb. Note the 30 degree spacing between voltage phasors and current phasors when we have unity power factor.

## Slide 21: Phasors for Source & Meter
IC
IA
A
B
C
A-B-C
+
+
+
+
C
A
B
Source
EBA
I
C
IA
EAC
ECB
IB
(30° + )
(30° + )
(30° + )
EBA
I
C
IA
Meter
ECB
EBC
(30° + )
(30° - )
Notes: Presenter
2019-08-21 16:57:46
--------------------------------------------
Source and meter phasors for A-B-C phase sequence.

## Slide 22: Phase Sequence CBA
C-B-A
IC
IA
B
A
C
+
+
+
C +
A
B
C-B-A
Meter Phasors
E
BA
IC
IA
EBC
(30° + )
(30° - )
Notes: Presenter
2019-08-21 16:57:46
--------------------------------------------
Meter Phasors for C-B-A phase sequence.

## Slide 23: Common Distribution Circuits
 | 240 V |  | 240 V | 
240 V |  |  |  | 
Three-Wire Network
Three-Wire Single Phase
Two-Wire Single Phase
Three-Wire Three Phase Delta
120V
120 V
120 V
120 V
208 V
208 V
208 V
Four-Wire Three Phase Wye
Four-Wire Three Phase Delta
240 V
240 V
240 V
120 V
120 V
208 V
120 V
208 V
120 V
120 V
120 V
240 V
Notes: Presenter
2019-08-21 16:57:47
--------------------------------------------
We can distinguish between service types just by measuring the magnitude of voltages between wires.

## Slide 24: 1 Expected Meter Phasors
(BALANCED LOAD AT POWER FACTOR = 1, ABC PHASE SEQUENCE)
2 wire, 1 
3 wire, 1 
270°
90°
180°
0°
1 Element
270°
90°
2 Element
180°
0°
270°
90°
1½ Element
0°
270°
90°
1 Element
Va
Va
Va
V
a
Ia
Ia
Ia
I
a
Vc
Ic
Ic
A-B-C
Notes: Presenter
2019-08-21 16:57:47
--------------------------------------------
Form 2S and 4S are 1 1/2 element meters. Form 1S and 3S are 1 element meters.

## Slide 25: 2 Element Expected Meter Phasors
3 wire, delta
3 wire, network
270
°
90°
Va
I
a
V
c
I
c
270
°
90°
Va
Ia
V
c
I
c
A-B-C
90°
180
°
0°
Va
Ia
270
°
V
cIc
4 wire, delta
4 wire, wye
270
°
90°
Va
I
a
V
c
Ic
(Balanced load at Power Factor = 1, ABC Phase Sequence)
Notes: Presenter
2019-08-21 16:57:47
--------------------------------------------
Form 45S & Form 56S meters (transformer rated) expect to be used on: 4 wire, wye; 4 wire, delta; or 3 wire delta Form 12S & Form 13A meters (self contained) expect to be used on: 3 wire delta; or 3 wire network

## Slide 26: Expected Meter Phasors
(AT POWER FACTOR = 1, ABC PHASE SEQUENCE)
3 wire, delta
3 wire, network
90°
180
°
0°
2 Element
270
°
180
°
0°
90°
2 Element
Va
Va
Ia
I
a
270
°
Vc
Vc
Ic
Ic
A-B-C

## Slide 27: 3 Element Expected Meter Phasors
4 wire, wye
4 wire, delta
270°
V
a
V
b
I
a
Ib
Vc
Ic
90°
Balanced Polyphase Load
270°
Va
Ia
Vb
I
b
Vc
Ic
90°
Balanced Polyphase Load
A-B-C
270°
V
a
Vc
Vb
Ia
Ib
90°
Single phase Load
Connected A to B
270°
Va
I
a
Vb
I
b
Vc
90°
Single phase Load
Connected A to B
(at Power Factor = 1, ABC Phase Sequence)
Notes: Presenter
2019-08-21 16:57:47
--------------------------------------------
3 Element meters may be used on 4 Wire, Wye or 4 Wire, Delta services.
Wide Voltage range 3 element meters are available as Form 9S, 16S, 10A or 48A.
Note that the current phasors are very different for single phase loading vs. polyphase loading.
The single phase loading on the wye service could be a control circuit or system on a 480 volt self contained service the feeds a predominantly motor load. The single phase loading on the delta service could be lighting load on a 240 volt delta service.

## Slide 28: Expected Meter Phasors
(AT POWER FACTOR = 1, ABC PHASE SEQUENCE)
90°
90°
2½ Element
270
°
180
°
0°
90°
3 Element
4 wire, wye
4 wire, delta
3 Element
Va
V
b
Ia
Ib
270
°
V
c Ic
Va
V
a
Ia
Ia
V
b
Ib
270
°
V
c Ic
I
b
V
c
270
°
90°
2 Element
Va
I
a
V
c
Ic
Ic
90°
2 Element
180
°
0°
Va
Ia
270
°
V
cIc
A-B-C

## Slide 29
Let's Talk about Why We Need to Understand
Vectors.

## Slide 30: Vector Addition

## Slide 31: Vector Subtraction

## Slide 32: AC Powers
Phasor (S)
Reactive (Q*)
Active (P)
*Not the “Q” of Q-hour metering
34
3

## Slide 33: AC Powers
Phasor (S)
Reactive (Q*)
Apparent (U)
Distortion (D)
Active (P)
*Not the “Q” of Q-hour metering
3

## Slide 34: How is 3 Apparent Power calculated?
To calculate Apparent power (U), first add the components for the phases together,
U
3
Notes: Presenter
2019-08-21 16:57:48
--------------------------------------------
This 3diagram shows that the length of the 3 U vectors (Arithmetic Apparent power) is longer than the U vector for the 3system.
The U vector for the 3 phase system is the vector addition of the 3 single phase U vectors.
Adding the magnitudes of the U vectors, we get Arithmetic Apparent power (U’ is not show in the diagram).
Using Vector addition to sum the U vectors, we get Apparent power.

## Slide 35: How is 3 Apparent Power calculated?
To calculate Apparent power (U), first add the components for the phases together,
U
U
3
Notes: Presenter
2019-08-21 16:57:48
--------------------------------------------
This 3diagram shows that the length of the 3 U vectors (Arithmetic Apparent power) is longer than the U vector for the 3system.
The U vector for the 3 phase system is the vector addition of the 3 single phase U vectors.
Adding the magnitudes of the U vectors, we get Arithmetic Apparent power (U’ is not show in the diagram).
Using Vector addition to sum the U vectors, we get Apparent power.

## Slide 36
To calculate Apparent power (U), first add the components for the phases together, then solve for U.
U3

U
P
A
A
B
C
A
B
C
2
2
2
 PB  PC  Q
 Q  Q
 D  D  D
3



A B C A B
3
C
S  P  P  P  Q
 Q  Q
2
2
U(arith) = UA + UB + UC
How is 3 Apparent Power calculated?
Notes: Presenter
2019-08-21 16:57:48
--------------------------------------------
This 3diagram shows that the length of the 3 U vectors (Arithmetic Apparent power) is longer than the U vector for the 3system.
The U vector for the 3 phase system is the vector addition of the 3 single phase U vectors.
Adding the magnitudes of the U vectors, we get Arithmetic Apparent power (U’ is not show in the diagram).
Using Vector addition to sum the U vectors, we get Apparent power.

## Slide 37: Apparent Power vs. Arithmetic Apparent Power
To calculate Apparent power (U), first add the components for the phases together, then solve for U.

U
A
B
C
A
B
C
2 2
2
3

PA  PB  PC
 Q
 Q
 Q  D
 D  D
To calculate Arithmetic Apparent power, add the Apparent power magnitudes of the three individual phases.
UArithmetic
 UA  UB  UC
UA
UB
UC
U
3
3
Notes: Presenter
2019-08-21 16:57:48
--------------------------------------------
This 3diagram shows that the length of the 3 U vectors (Arithmetic Apparent power) is longer than the U vector for the 3system.
The U vector for the 3 phase system is the vector addition of the 3 single phase U vectors.
Adding the magnitudes of the U vectors, we get Arithmetic Apparent power (U’ is not show in the diagram).
Using Vector addition to sum the U vectors, we get Apparent power.

## Slide 38: All KVAs are not Created Equal
3
Power Calculations POWERS Phase A Phase B Phase C Total Active (P) 3626.4 2880.0 2833.0 9339.4 Reactive (Q) 317.3 2146.0 2112.0 4575.3 Distortion (D) 0.0 1102.6 1784.5 2887.1 Apparent (U) 3640 3757 3959 |  |  |  | 
PHASOR (S) | (VA)Total | = | 10,400 | PF = 89.8
APPARENT (U) | (VA)Total | = | 10,793 | PF = 86.5
ARITH. (Uarth) | (VA)Total | = | 11,356 | PF = 82.2

## Slide 39: Modern Reactive Metering
3
Which “kVA” calculation method is correct?
  They all are “correct”, by definition.
  Each utility needs to decide which value is appropriate for their own needs.
  Phasor Power is what results from calculations based on traditional kWh and kvarh meter readings, using a Phase- Shifting Transformer.
  Apparent Power provides more complete picture of “cost of service”, expected answers under all conditions.
  Arithmetic Apparent Power may provide unexpected results (low PF, high kVA) for asymmetrical or unbalanced conditions.

## Slide 40: Phase “X” Formulae
(kVA)
3
Nonreactive Power,
(kVA) (a.k.a." Fuzzy var s")
Fictitious Power,
(kVA)
Phasor Power,
(kVA)
Distortion Power,
Re active Power,
Active Power,
Apparent Power,
RMS Current,
RMS Potential,
F U
N U
P
S
D U
E I
Q
E I
P
I
I
E
E
X
2
X
X
2
X
2
X
X
X
2
X
X
X
2
X
2
X
X
Xh Xh
X
Xh
Xh
Xh Xh
 Q2
X
H
2
Xh
X
H
2
Xh

h1
X
 
 P
 
 Q2
 
 Q2
 P
 
U X  EX I X
H
 
h1
H
 
h1
 |  | (Volts)
 |  | ( Amperes)
cos |    | (kVA) (kW )
sin Xh    (k var) Xh |  | 



h1
Exh and Ixh are the RMS voltage and amperage of harmonic h. xh and xh are the phase angles of the voltage and current of harmonic h with respect to the reference time-frame. H is the highest harmonic ordinal.

## Slide 41: Different Meters
Aclara kV2c Meter
Landis + Gyr S4e
Sensus Icon APX
Itron Sentinel
3
Honeywell A3

## Slide 42: Phase Rotation & Site Measurements
Notes: Presenter
2019-08-21 16:57:42
--------------------------------------------
The time domain representation becomes difficult to use when 3 phases are shown on one diagram. The Phasor representation shows the same 3 phase service and is easier to digest quickly.

## Slide 43: Step 1: Draw Diagram for...
Phasor Construction
Power
Transformer
Meter Load
43

## Slide 44: Step 2: Draw Diagram for...
Step 2: Label points of Power Transformer
Phasor Construction
Power
Transformer
Meter Load
A
B
C
44

## Slide 45: Step 3: Draw and Label all Line Currents
Power Meter Load
Transformer
IA
A
B
C
Draw line currents between power transformer and meter. Use arrows with closed points (
Assume all currents flow from transformer to load. Where necessary, draw power transformer coil currents and label with double subscript notation (IBA, IAC, etc.
Phasor Construction
).
IC
45
IB

## Slide 46: Step 4: Mark Polarity on all Current Coils
The polarity mark (+) goes on the line side of all current coils except: (a): For 2 1/2 stator Z-coil meters. The polarity “+” goes on the
load side of the Z-coil.
(b): For 3-wire, 1-phase meters and the 3-wire stator on the left side of a 4-wire delta meter, the “+” goes on the load side of the right hand coil of the single stator meter, and the “inside” coil of the left hand stator in the 4-wire delta meter.
Phasor Construction
Power Meter Load
Transformer
IA
A
B
C
I
46
C
+
+

## Slide 47: Step 4: Polarity of Current Coils (cont.)
If line current enters the “+” end of a current coil, the coil current is assumed to be in phase with the line current. If, however, the current enters the unmarked end of the coil, the current is assumed to be 180° out of phase with the line current.
Phasor Construction
Power Meter Load
Transformer
IA
A
B
C
I
47
C
+
+

## Slide 48: Step 5: Mark Polarity on all Voltage Coils
The polarity mark (+) goes on the end of the voltage coil that connects to the “+” end of the current coil.
Phasor Construction
Power Meter Load
Transformer
+
+
IA
A
B
C
I
48
C
+
+

## Slide 49: Step 6: Draw Voltage Arrows at Power Transformer
Draw open ended arrows to represent voltage at the power transformer.
Wye-connected: point away from the neutral.
Delta-connected: tracing tail-to-head-to-tail, etc., around the delta following a counter-clockwise direction.
Phasor Construction
Power Meter Load
Transformer
+
+
IA
A
B
C
I
C
+
+
49

## Slide 50: Step 7: Establish Voltage & Current Relationships
Phasor Construction
Use Kirchoff’s Laws to establish the needed relationships between voltages and currents at the power transformer.
+
+
IA
A
B
C
IC
+
+
50

## Slide 51: Step 8: Complete the “Source” Phasors
Phasor Construction
Power Meter Load Transformer
IA
A
B
C
A-B-C
+
+
+
C
51
A
B
IC
+
Complete the phasor diagram for the power transformer (source).

## Slide 52: Step 8: Complete the “Source” Phasors
Phasor Construction
Power Meter Load Transformer
IA
A
B
C
A-B-C
+
+
+
C
A
B
IC
+
I
ECB
52
A
IC
IB
EBA
EAC

## Slide 53: Step 9: Construct Meter Voltage Phasors
Draw the voltage phasors for the meter, using the tracing method.
Starting at the polarity end of the voltage coil, trace through the voltage coil, back through the source, and return to the polarity end of the voltage coil.
The direction of the METER phasor is the direction traveled through the source transformer.
Phasor Construction
Power Meter Load Transformer
IA
A
B
C
A-B-C
+
+
+
C
53
A
B
IC
+

## Slide 54: Step 9: Construct Meter Voltage Phasors
Phasor Construction
Power Meter Load Transformer
IA
A
B
C
A-B-C
+
+
+
C
A
B
IC
+
I
A
IC
IB
EB
A
EC
EA
C
EB
C
EB
A
54
B

## Slide 55: Step 10: Construct Meter Current Phasors
Phasor Construction
Power Meter Load Transformer
IA
A
B
C
A-B-C
+
+
+
C
55
A
B
IC
+
Add meter current phasors by using the relationships developed in step 8, and observing the polarity marks of the current coils. Make sure all voltage and current phasors are labeled,
and show the interactions between voltages and currents in the meter stators by connecting the appropriate phasors with elongated ellipses.

## Slide 56: Step 10: Construct Meter Current Phasors
Phasor Construction
Power Meter Load Transformer
I
A
A
B
C
A-B-C
+
+
+
C
A
B
IC
+
IA
IC
I
B
E
B
A
EC
B
EA
C
VA
VC
IA
IC
56

## Slide 57: Step 11: Write Equation for Meter Watts
Phasor Construction
Power Meter Load Transformer
IA
A
B
C
A-B-C
+
+
+
C
A
B
IC
+
VA
IA
Show the expression for the Meter Watts.
VC
IC
57

## Slide 58: Step 11: Write Equation for Meter Watts
Power Meter Load Transformer
IA
A
B
C
A-B-C
+
+
+
+
C
A
B
IC
 V LL I L cos(30  ) V LL I L cos(30  )
V LL I L cos 30 cos  sin 30 sin  cos 30 cos  sin 30 sin 
Show the expression for the Meter Watts.
MeterWatts  V A I A cos(30  A) V C I C cos(30  C )
3 3

 
 

 3V LL I L cos
 
V LL I L  2 cos    2 cos 
VA
VC
IA
IC
Assuming balanced 3-phase load and balanced voltages
Phasor Construction
58

## Slide 59: Step 12: Write Equation for Load Watts
Phasor Construction
Power Meter Load Transformer
IA
A
B
C
A-B-C
+
+
+
C
59
A
B
IC
+
Show the expression for the Delivered Watts, or Load Watts.

## Slide 60: Step 12: Write Equation for Load Watts
Phasor Construction
Power Meter Load Transformer
IA
A
B
C
A-B-C
+
+
+
C
A
B
IC
+
Show the expression for the Delivered Watts, or Load Watts.
3V LL I L cos( )
60
Load Watts 
For a balanced 3-phase load:

## Slide 61: Step 13: Calculate “Percent Registration”
Phasor Construction
Power Meter Load Transformer
IA
A
B
C
A-B-C
+
+
+
C
61
A
B
IC
+
Calculate the percent registration of the meter by dividing the Meter Watts by the Load Watts, then multiplying the result by 100%.

## Slide 62: Step 13: Calculate “Percent Registration”
Phasor Construction
Power Meter Load Transformer
IA
A
B
C
A-B-C
+
+
+
C
A
B
Calculate the percent registration of the meter by dividing the Meter Watts
by the Load Watts, then multiplying the result by 100%.
IC
+
cos
62
3V
 100%
100%
Load Watts
Meter Watts
Percent Registration 
LL I L
 3V LL I L cos 100%

## Slide 63: Questions?
64
Carl Chermak
TESCO – The Eastern Specialty Company
Bristol, PA
215-228-0500
This presentation can also be found under Meter Conferences and Schools on the TESCO website: tescometering.com